|  |  |
| --- | --- |
| BR 210 095 | PremiumLine safety eye shower with two spray heads 45°, wall mounted |
| PremiumLine safety eye shower with two spray heads 45°, wall mounted- connection pipe of stainless steel for easy installation and alignment of the shower, polished, water inlet ¾” male- ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated- push plate made of stainless steel, polished, length 130 mm, with large signal "PUSH", luminescent according to DIN 67510- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure- high-performance spray heads made of stainless steel for large-scale dispersion of water, polished, 45° angled, with plastic spray plate, low calcification, rubber sleeves and sealed dust caps, mounted over distributor fork - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- height 200 mm, projection 310 mm, total width incl. lever 250 mm- mounting height 900 mm (± 200 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014 and EN 15154-2:2006- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 210 095**Technical Specifications**Minimum flow pressure: 1.5 barOperating pressure: 1.5 to 5 barFlow rate: 14 l/minWater inlet: 3/4” maleDimensions (H x W x D): 200 x 250 x 310 mm |