|  |  |
| --- | --- |
| BR 300 085 | ClassicLine safety eye shower with bowl, wall mounted, exposed pipework |
| ClassicLine safety eye shower with bowl, wall mounted, exposed pipework- wall flange with 4 mounting holes made of stainless steel, chemical resistant green powder coated, water inlet ¾” female- connection pipe of stainless steel for easy installation and alignment of the shower, chemical resistant green powder coated- ball valve ½” of stainless steel, with PUSH-lever actuation, DIN-DVGW tested and certificated- push plate made of steel, chemical resistant green powder coated, length 240 mm, with large signal "PUSH", luminescent according to DIN 67510- integrated flow regulation 14 litre / minute for a standard-compliant jet pattern at a specified working range of 2.5 to 5 bar flow pressure- high-performance spray heads for large-scale dispersion of water, with plastic spray plate, low calcification, incl. rubber sleeves and sealed dust caps, mounted over distributor fork- bowl made of plastic, green, diameter 275 mm, water outlet 1 ¼” male- sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre- height 210 mm, projection 415 mm, total width incl. lever 410 mm- mounting height 860 mm (± 200 mm)- according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014 and EN 15154-2:2006- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 300 085**Technical Specifications**Minimum flow pressure: 2.5 barOperating pressure: 2.5 to 5 barFlow rate: 14 l/minWater inlet: ¾” femaleWater outlet: 1 ¼“ maleDimensions (H x W x D): 210 x 410 x 415 mm |