|  |  |
| --- | --- |
| BR 713 025 | ClassicLine hand-held eye shower with one spray head 45°, wall or table mounted |
| ClassicLine hand-held eye shower with one spray head 45°, wall or table mounted  - ergonomically shaped handle with integrated, adjusting activation made of plastics, valve not self-closing  - high-performance spray head for large-scale dispersion of water, 45° angled, with plastic spray plate, largely free of calcification, with rubber sleeves and sealed dust caps - integrated flow regulation 7 litre / minute for a standard-compliant jet pattern at a specified working range of 1.5 to 5 bar flow pressure - integrated backflow preventer to protect the drinking water - stainless steel covered hose, length 1.5 meter, water inlet ½” female, DIN-DVGW tested and certificated  - robust table and wall mounting bracket with positioning of the shower, accessories M28x1,5x80mm made of stainless steel, incl. fastening-parts kit with nut M28x1,5mm and 2 screws M5 for mounting difficult to access, sealing to table surface with O-Ring  - sign for eye shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 100 x 100 mm, viewing distance 10 metre  - mounting height 750 mm (± 200 mm) - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014 and EN 15154-2:2006 - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 713 025  **Technical Specifications**  Minimum flow pressure: 1.5 bar  Operating pressure: 1.5 to 5 bar  Flow rate: 7 l/min  Water inlet: ½“ female  Dimensions (H x W x D): 270 x 65 x 65 mm | |