|  |  |
| --- | --- |
| BR 818 095 | PremiumLine freestanding frostprotected heated body safety shower with eye-/face wash unit with bowl and lid |
| PremiumLine frostprotected heated body safety shower with eye-/face wash unit with bowl and lid, floor mounted  - base plate with 4 mounting holes of stainless steel, dimensions 200 x 200 mm  - stand pipe 1 ¼” of stainless steel two-part, with bottom water inlet 1 ¼” female, total height 2300 mm  - connection pipe 1 ¼” of stainless steel, length 75 mm  - ball valve 1 ¼” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated  - pull rod with ring handle of stainless steel, length 700 mm  - wall shower arm 1 ¼” of stainless steel, projection 600 mm  - high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining  - insulation made of mineral wool shape package, non-flammable, according to DIN 4102  - heating by self-regulating trace tape, body shower output 10 W/m, eye shower output 25W/m, electrical supply 230 V - 50 Hz  - outdoor thermostat and power-saving-circuit (shutdown of trace tape at 11°C, switch on at 4°C)  - outer casing of the shower made of screwed stainless steel housing, easy to dismantle for maintenance work, including green/white indicator strips for better visibility of the shower  - sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 meter  - integrated PremiumLine eye-/face wash unit with bowl and lid for mounting on standpipe, position and orientation freely selectable  - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male  - integrated protective cover against dust  - actuation by pulling down the lid  - ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated  - aerators made of brass with a very limited spray pattern, chrome-plated  - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male  - inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 meter  - suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection  - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717  - according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019  - DIN-DVGW tested and certificated  Manufacturer: B-SAFETY or equal  Article-No.: BR 818 095  **Technical Specifications**  Minimum flow pressure: 2.0 bar  Operating pressure: 2 to 8 bar  Flow rate body shower: 50 l/min  Water inlet: 1 ¼” male  Electrical supply: 230 V - 50 Hz  Dimensions: (H x W x D): 2300 x 378 x 806 mm  **Technical specifications eye shower**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14-20 l/min  Water outlet: 1 1/2” male  **Product overview**  **BR 818 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)  **BR 818 095/ 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) | |