|  |  |
| --- | --- |
| BR 818 095 | PremiumLine freestanding frostprotected heated body safety shower with eye-/face wash unit with bowl and lid |
| PremiumLine frostprotected heated body safety shower with eye-/face wash unit with bowl and lid, floor mounted- base plate with 4 mounting holes of stainless steel, dimensions 200 x 200 mm- stand pipe 1 ¼” of stainless steel two-part, with bottom water inlet 1 ¼” female, total height 2300 mm- connection pipe 1 ¼” of stainless steel, length 75 mm- ball valve 1 ¼” of stainless steel, with pull rod actuation, DIN-DVGW tested and certificated- pull rod with ring handle of stainless steel, length 700 mm- wall shower arm 1 ¼” of stainless steel, projection 600 mm- high-performance shower head of chemical resistant plastics, black, with improved spray pattern, corrosion resistant, largely calcification- and maintenance-free, very robust, self-draining- insulation made of mineral wool shape package, non-flammable, according to DIN 4102- heating by self-regulating trace tape, body shower output 10 W/m, eye shower output 25W/m, electrical supply 230 V - 50 Hz- outdoor thermostat and power-saving-circuit (shutdown of trace tape at 11°C, switch on at 4°C)- outer casing of the shower made of screwed stainless steel housing, easy to dismantle for maintenance work, including green/white indicator strips for better visibility of the shower- sign for body safety shower according to EN ISO 7010 und ASR A1.3, self-adhesive PVC-film, 150 x 150 mm, viewing distance 15 meter- integrated PremiumLine eye-/face wash unit with bowl and lid for mounting on standpipe, position and orientation freely selectable- housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male- integrated protective cover against dust- actuation by pulling down the lid- ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated- aerators made of brass with a very limited spray pattern, chrome-plated- with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male- inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 meter- suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014, EN 15154-1:2006, EN 15154-2:2006 and EN 15154-5:2019- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 818 095**Technical Specifications**Minimum flow pressure: 2.0 barOperating pressure: 2 to 8 barFlow rate body shower: 50 l/minWater inlet: 1 ¼” maleElectrical supply: 230 V - 50 HzDimensions: (H x W x D): 2300 x 378 x 806 mm**Technical specifications eye shower**Minimum flow pressure: 2.5 barOperating pressure: 2.5 to 5 barFlow rate: 14-20 l/minWater outlet: 1 1/2” male**Product overview****BR 818 095:** flow rate 50 l/min (hazard class I according to EN 15154-5:2019)**BR 818 095/ 110L:** flow rate 110 l/min (hazard class III according to EN 15154-5:2019) |