|  |  |
| --- | --- |
| BR 826 095 | PremiumLine frostprotected heated eye-/face wash unit with bowl and lid, wall mounted, exposed pipework |
| PremiumLine frostprotected heated eye-/face wash unit with bowl and lid, wall mounted, exposed pipework- housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male- integrated protective cover against dust- actuation by pulling down the lid- ball valve 3/8“ of stainless steel, with lever actuation by lid, DIN-DVGW tested and certificated- aerators made of brass with a very limited spray pattern, chrome-plated- with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male- insulation made of mineral wool shape package, non-flammable, according to DIN 4102- heating by self-regulating trace tape, output 23 W/m, electrical supply 230 V - 50 Hz- outdoor thermostat and power-saving-circuit (shutdown of trace tape at 14°C, switch on at 4°C)- inclusive sign for eye shower according to EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre- height 245 mm, width 356 mm, depth 305 mm- mounting height (lower edge) 910 mm (± 200 mm)- suitable for use in EX-Zones 1 & 2, all electrical parts explosion-proof, with risk assessment in accordance with industrial safety regulations concerning the non-electrical and electrical explosion protection - according to BGI/GUV-I 850-0, DIN 1988 and EN 1717- according to ANSI Z358.1-2014 and EN 15154-2:2006- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 826 095**Technical Specifications**Minimum flow pressure: 2.5 barOperating pressure: 2.5 to 5 barFlow rate: 14-20 l/minWater inlet: 3/8” maleWater outlet: 1 ½” maleElectrical supply: 230 V - 50 HzDimensions (H x W x D): 245 x 356 x 305 mm |