|  |  |
| --- | --- |
| BR 852 085 | ClassicLine eye-/face wash unit with bowl and lid, floor mounted |
| ClassicLine eye-/face wash unit with bowl and lid, floor mounted  - base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, dimensions 200 x 200 mm  - stand pipe 1 ¼” of stainless steel, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 1025 mm  - housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male  - integrated protective cover against dust  - actuation by pulling down the lid - ball valve 3/8“ of brass, with lever actuation by lid, DIN-DVGW tested and certificated  - aerators made of brass with a very limited spray pattern, chrome-plated  - with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male  - inclusive sign for eye shower according to DIN EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre  - height 970 mm, width 356 mm, depth 390 mm  - mounting height (lower edge) 910 mm (± 200 mm)  - according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717  - according to ANSI Z358.1-2014 and DIN EN 15154-2:2006  - DIN-DVGW tested and certificated Manufacturer: B-SAFETY or equal Article-No.: BR 852 085  **Technical Specifications**  Minimum flow pressure: 2.5 bar  Operating pressure: 2.5 to 5 bar  Flow rate: 14-20 l/min  Water inlet: 1 ¼” female  Water outlet: 1 ½” male  Dimensions (H x W x D): 970 x 356 x 390 mm | |