|  |  |
| --- | --- |
| BR 852 085 | ClassicLine eye-/face wash unit with bowl and lid, floor mounted |
| ClassicLine eye-/face wash unit with bowl and lid, floor mounted- base plate with 4 mounting holes of stainless steel, chemical resistant green powder coated, dimensions 200 x 200 mm- stand pipe 1 ¼” of stainless steel, chemical resistant green powder coated, with top and bottom water inlet 1 ¼” female, total height 1025 mm- housing, lid and bowl made of UV and impact resistant ABS plastics, water outlet 1 ½“ male- integrated protective cover against dust- actuation by pulling down the lid- ball valve 3/8“ of brass, with lever actuation by lid, DIN-DVGW tested and certificated- aerators made of brass with a very limited spray pattern, chrome-plated- with integrated flow regulation valve 3/8” for setting the desired spray height and flow rate, water inlet 3/8” male- inclusive sign for eye shower according to DIN EN ISO 7010 und ASR A1.3 on the lid, dimensions 170 x 170 mm, viewing distance 17 metre- height 970 mm, width 356 mm, depth 390 mm- mounting height (lower edge) 910 mm (± 200 mm)- according to BGI/GUV-I 850-0, DIN 1988 and DIN EN 1717- according to ANSI Z358.1-2014 and DIN EN 15154-2:2006- DIN-DVGW tested and certificatedManufacturer: B-SAFETY or equalArticle-No.: BR 852 085**Technical Specifications**Minimum flow pressure: 2.5 barOperating pressure: 2.5 to 5 barFlow rate: 14-20 l/minWater inlet: 1 ¼” femaleWater outlet: 1 ½” maleDimensions (H x W x D): 970 x 356 x 390 mm |